SECTION 08 12 13 HOLLOW METAL FRAMES

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes the following:

          - Standard hollow metal door frames.

          - Standard hollow metal sidelight frames

          - Standard hollow metal borrowed-light frames.

          - Standard hollow metal fire-rated frame assemblies.

        - Related Requirements:

RETAIN SUBPARAGRAPHS BELOW TO CROSS-REFERENCE REQUIREMENTS CONTRACTOR MIGHT EXPECT TO FIND IN THIS SECTION BUT ARE SPECIFIED IN OTHER SECTIONS.

          - Section 08 11 13 "Hollow Metal Doors and Frames" for hollow-metal door and frame assemblies.

          - Section 08 14 16 "Flush Wood Doors" for wood doors installed in hollow-metal frames.

      - DEFINITIONS

        - Minimum Thickness:  Minimum thickness of base metal without coatings according to SDI A250.8.

      - COORDINATION

        - Coordinate anchorage installation for hollow-metal frames.  Furnish setting drawings, templates, and directions for installing anchorages, including sleeves, concrete inserts, anchor bolts, and items with integral anchors.  Deliver such items to Project site in time for installation.

      - PREINSTALLATION MEETINGS

RETAIN "PREINSTALLATION CONFERENCE" PARAGRAPH BELOW IF WORK OF THIS SECTION IS EXTENSIVE OR COMPLEX ENOUGH TO JUSTIFY A CONFERENCE.

        - Preinstallation Conference:  Conduct conference at Project site.

      - SUBMITTALS

        - Product Data:  For each type of product.

          - Include construction details, material descriptions, fire-resistance ratings, temperature-rise ratings, and finishes.

        - Shop Drawings:  Include the following:

          - Frame details for each frame type, including dimensioned profiles and metal thicknesses.

          - Locations of reinforcement and preparations for hardware.

          - Details of each different wall opening condition.

          - Details of anchorages, joints, field splices, and connections.

          - Details of moldings, removable stops, and glazing.

          - Details of conduit and preparations for power, signal, and control systems.

        - Schedule:  Provide a schedule of hollow-metal work prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings.  Coordinate with final Door Hardware Schedule.

        - Product Test Reports:  For each type of frame assembly, for tests performed by a qualified testing agency.

DOORS OVER 4-FEET X 10-FEET PER LEAF OR 40 SQ. FT. ARE CONSIDERED TO BE OVERSIZED. DELETE IF NOT NEEDED.

        - Oversize Construction Certification:  For assemblies required to be fire rated and exceeding limitations of labeled assemblies.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver hollow-metal work palletized, packaged, or crated to provide protection during transit and Project-site storage.  Do not use nonvented plastic.

          - Provide additional protection to prevent damage to factory-finished units.

        - Deliver welded frames with two removable spreader bars across bottom of frames, tack welded to jambs and mullions.

        - Store hollow-metal work vertically under cover at Project site with head up.  Place on minimum 4-inch- (102-mm-) high wood blocking.  Provide minimum 1/4-inch (6-mm) space between each unit to permit air circulation.

- PRODUCTS

      - MANUFACTURERS

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - Amweld International, LLC.

          - Ceco Door Products; an Assa Abloy Group company.

          - Curries Company; an Assa Abloy Group company.

          - Mesker Door Inc.

          - Pioneer Industries, Inc.

          - Republic Doors and Frames.

          - Steelcraft; an Ingersoll-Rand company.

        - Source Limitations:  Obtain hollow-metal work from single source from single manufacturer.

      - REGULATORY REQUIREMENTS

        - Fire-Rated Assemblies:  Complying with NFPA 80 and listed and labeled by a qualified testing agency acceptable to authorities having jurisdiction for fire-protection ratings and temperature-rise limits indicated, based on testing at positive pressure according to NFPA 252 or UL 10C.

          - Smoke- and Draft-Control Assemblies:  Provide an assembly with gaskets listed and labeled for smoke and draft control by a qualified testing agency acceptable to authorities having jurisdiction, based on testing according to UL 1784 and installed in compliance with NFPA 105.

        - Fire-Rated, Borrowed-Light Assemblies:  Complying with NFPA 80 and listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction for fire-protection ratings indicated, based on testing according to NFPA 257 or UL 9.

      - INTERIOR FRAMES

        - Construct interior frames to comply with the standards indicated for materials, fabrication, hardware locations, hardware reinforcement, tolerances, and clearances, and as specified.

        - Heavy-Duty Frames:  SDI A250.8, Level 2.

          - Physical Performance:  Level B according to SDI A250.4.

          - Materials:  Uncoated steel sheet, minimum thickness of 0.053 inch (1.3 mm).

          - Construction:  Face welded.

          - Throat Width:  Coordinate throat width with partition thickness, increase throat width to accommodate heavy gage metal studs.

          - Exposed Finish:  Prime.

      - EXTERIOR HOLLOW-METAL FRAMES

        - Construct exterior frames to comply with the standards indicated for materials, fabrication, hardware locations, hardware reinforcement, tolerances, and clearances, and as specified.

        - Extra-Heavy-Duty Frames:  SDI A250.8, Level 3.

          - Physical Performance:  Level A according to SDI A250.4.

          - Materials:  Metallic-coated steel sheet, minimum thickness of 0.053 inch (1.3 mm), with minimum A40 (ZF120) coating.

          - Construction:  Full profile welded.

          - Exposed Finish:  Prime.

KEEP PARAGRAPH BELOW FOR THERMALLY BROKEN FRAMES.

        - Thermally Broken Frames:

          - Materials:  Metallic-coated steel sheet, minimum thickness of 0.053 inch (1.3 mm), with minimum A40 (ZF120) coating.

          - Interior and exterior sections shall be separated by a continuous break with integral PVC, EPDM, silicone, or thermoplastic polyolefin rubber thermal break material. Frame shall have kerfs to accept weather-stripping.

          - Closed sections shall be factory insulated.

          - Provide thermal insulation for open sections.

          - Construction:  Full profile welded.

          - Exposed Finish:  Prime.

      - FRAME ANCHORS

        - Jamb Anchors:

          - Masonry Type:  Adjustable strap-and-stirrup or T-shaped anchors to suit frame size, not less than 0.042 inch (1.0 mm) thick, with corrugated or perforated straps not less than 2 inches (51 mm) wide by 10 inches (254 mm) long; or wire anchors not less than 0.177 inch (4.5 mm) thick.

          - Stud-Wall Type:  Designed to engage stud, welded to back of frames; not less than 0.042 inch (1.0 mm) thick.

          - Postinstalled Expansion Type for In-Place Concrete or Masonry:  Minimum 3/8-inch- (9.5-mm-) diameter bolts with expansion shields or inserts.  Provide pipe spacer from frame to wall, with throat reinforcement plate, welded to frame at each anchor location.

        - Floor Anchors:  Formed from same material as frames, minimum thickness of 0.042 inch (1.0 mm), and as follows:

          - Monolithic Concrete Slabs:  Clip-type anchors, with two holes to receive fasteners.

          - Separate Topping Concrete Slabs:  Adjustable-type anchors with extension clips, allowing not less than 2-inch (51-mm) height adjustment.  Terminate bottom of frames at finish floor surface.

      - MATERIALS

        - Cold-Rolled Steel Sheet:  ASTM A 1008/A 1008M, Commercial Steel (CS), Type B; suitable for exposed applications.

        - Hot-Rolled Steel Sheet:  ASTM A 1011/A 1011M, Commercial Steel (CS), Type B; free of scale, pitting, or surface defects; pickled and oiled.

        - Metallic-Coated Steel Sheet:  ASTM A 653/A 653M, Commercial Steel (CS), Type B.

        - Frame Anchors:  ASTM A 879/A 879M, Commercial Steel (CS), 04Z (12G) coating designation; mill phosphatized.

          - For anchors built into exterior walls, steel sheet complying with ASTM A 1008/A 1008M or ASTM A 1011/A 1011M, hot-dip galvanized according to ASTM A 153/A 153M, Class B.

        - Inserts, Bolts, and Fasteners:  Hot-dip galvanized according to ASTM A 153/A 153M.

        - Power-Actuated Fasteners in Concrete:  Fastener system of type suitable for application indicated, fabricated from corrosion-resistant materials, with clips or other accessory devices for attaching hollow-metal frames of type indicated.

RETAIN "GROUT" PARAGRAPH BELOW FOR GROUTED FRAMES.  SDI RECOMMENDS THAT GROUT FOR HOLLOW-METAL FRAMES HAVE A MAXIMUM 4-INCH (102-MM) SLUMP.

        - Grout:  ASTM C 476, except with a maximum slump of 4 inches (102 mm), as measured according to ASTM C 143/C 143M.

        - Mineral-Fiber Insulation:  ASTM C 665, Type I (blankets without membrane facing); consisting of fibers manufactured from slag or rock wool with 6- to 12-lb/cu. ft. (96- to 192-kg/cu. m) density; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; passing ASTM E 136 for combustion characteristics.

        - Glazing:  Comply with requirements in Section 088000 "Glazing."

RETAIN "BITUMINOUS COATING" PARAGRAPH BELOW IF REQUIRED FOR GROUTED FRAMES.

        - Bituminous Coating:  Cold-applied asphalt mastic, compounded for 15-mil (0.4-mm) dry film thickness per coat.  Provide inert-type noncorrosive compound free of asbestos fibers, sulfur components, and other deleterious impurities.

      - FABRICATION

        - Fabricate hollow-metal work to be rigid and free of defects, warp, or buckle.  Accurately form metal to required sizes and profiles, with minimum radius for metal thickness.  Where practical, fit and assemble units in manufacturer's plant.  To ensure proper assembly at Project site, clearly identify work that cannot be permanently factory assembled before shipment.

        - Hollow-Metal Frames:  Where frames are fabricated in sections due to shipping or handling limitations, provide alignment plates or angles at each joint, fabricated of same thickness metal as frames.

          - [Sidelight] [and] [Transom Bar] Frames:  Provide closed tubular members with no visible face seams or joints, fabricated from same material as door frame.  Fasten members at crossings and to jambs by butt welding.

          - Provide countersunk, flat- or oval-head exposed screws and bolts for exposed fasteners unless otherwise indicated.

          - Grout Guards:  Weld guards to frame at back of hardware mortises in frames to be grouted.

          - Floor Anchors:  Weld anchors to bottoms of jambs with at least four spot welds per anchor.

          - Jamb Anchors:  Provide number and spacing of anchors as follows:

            - Masonry Type:  Locate anchors not more than 16 inches (406 mm) from top and bottom of frame.  Space anchors not more than 32 inches (813 mm) o.c., to match coursing, and as follows:

              - Two anchors per jamb up to 60 inches (1524 mm) high.

              - Three anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

              - Four anchors per jamb from 90 to 120 inches (2286 to 3048 mm) high.

              - Four anchors per jamb plus one additional anchor per jamb for each 24 inches (610 mm) or fraction thereof above 120 inches (3048 mm) high.

            - Stud-Wall Type:  Locate anchors not more than 18 inches (457 mm) from top and bottom of frame.  Space anchors not more than 32 inches (813 mm) o.c. and as follows:

              - Three anchors per jamb up to 60 inches (1524 mm) high.

              - Four anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

              - Five anchors per jamb from 90 to 96 inches (2286 to 2438 mm) high.

              - Five anchors per jamb plus one additional anchor per jamb for each 24 inches (610 mm) or fraction thereof above 96 inches (2438 mm) high.

            - Postinstalled Expansion Type:  Locate anchors not more than 6 inches (152 mm) from top and bottom of frame.  Space anchors not more than 26 inches (660 mm) o.c.

          - Door Silencers:  Except on weather-stripped frames, drill stops to receive door silencers as follows.  Keep holes clear during construction.

            - Single-Door Frames:  Drill stop in strike jamb to receive three door silencers.

            - Double-Door Frames:  Drill stop in head jamb to receive two door silencers.

          - Terminated Stops:  Terminate stops 6 inches (152 mm) above finish floor with a 45-degree angle cut, and close open end of stop with steel sheet closure.  Cover opening in extension of frame with welded-steel filler plate, with welds ground smooth and flush with frame.

        - Hardware Preparation:  Factory prepare hollow-metal work to receive templated mortised hardware; include cutouts, reinforcement, mortising, drilling, and tapping according to SDI A250.6, the Door Hardware Schedule, and templates.

          - Reinforce frames to receive nontemplated, mortised, and surface-mounted hardware.

          - Comply with applicable requirements in SDI A250.6 and BHMA A156.115 for preparation of hollow-metal work for hardware.

        - Stops and Moldings:  Provide stops and moldings around glazed lites and louvers where indicated.  Form corners of stops and moldings with butted or mitered hairline joints.

          - Single Glazed Lites:  Provide fixed stops and moldings welded on secure side of hollow-metal work.

          - Multiple Glazed Lites:  Provide fixed and removable stops and moldings so that each glazed lite is capable of being removed independently.

          - Provide fixed frame moldings on outside of exterior and on secure side of interior frames.

          - Provide loose stops and moldings on inside of hollow-metal work.

          - Coordinate rabbet width between fixed and removable stops with glazing and installation types indicated.

      - STEEL FINISHES

        - Prime Finish:  Clean, pretreat, and apply manufacturer's standard primer.

          - Shop Primer:  Manufacturer's standard, fast-curing, lead- and chromate-free primer complying with SDI A250.10; recommended by primer manufacturer for substrate; compatible with substrate and field-applied coatings despite prolonged exposure.

      - ACCESSORIES

        - Mullions and Transom Bars:  Join to adjacent members by welding or rigid mechanical anchors.

        - Grout Guards:  Formed from same material as frames, not less than 0.016 inch (0.4 mm) thick.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for embedded and built-in anchors to verify actual locations before frame installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Remove welded-in shipping spreaders installed at factory.  Restore exposed finish by grinding, filling, and dressing, as required to make repaired area smooth, flush, and invisible on exposed faces.

        - Drill and tap frames to receive nontemplated, mortised, and surface-mounted hardware.

      - INSTALLATION

        - General:  Install hollow-metal work plumb, rigid, properly aligned, and securely fastened in place.  Comply with Drawings and manufacturer's written instructions.

        - Hollow-Metal Frames:  Install hollow-metal frames of size and profile indicated.  Comply with SDI A250.11 as required by standards specified.

          - Set frames accurately in position; plumbed, aligned, and braced securely until permanent anchors are set.  After wall construction is complete, remove temporary braces, leaving surfaces smooth and undamaged.

            - At fire-rated openings, install frames according to NFPA 80.

            - Where frames are fabricated in sections because of shipping or handling limitations, field splice at approved locations by welding face joint continuously; grind, fill, dress, and make splice smooth, flush, and invisible on exposed faces.

            - Install frames with removable stops located on secure side of opening.

            - Install door silencers in frames before grouting.

            - Remove temporary braces necessary for installation only after frames have been properly set and secured.

            - Check plumb, square, and twist of frames as walls are constructed.  Shim as necessary to comply with installation tolerances.

            - Field apply bituminous coating to backs of frames that will be filled with grout containing antifreezing agents.

          - Floor Anchors:  Provide floor anchors for each jamb and mullion that extends to floor, and secure with postinstalled expansion anchors.

RETAIN FIRST SUBPARAGRAPH BELOW IF PERMITTED.

            - Floor anchors may be set with power-actuated fasteners instead of postinstalled expansion anchors if so indicated and approved on Shop Drawings.

          - Metal-Stud Partitions:  Solidly pack mineral-fiber insulation inside frames.

          - Masonry Walls:  Coordinate installation of frames to allow for solidly filling space between frames and masonry with grout.

          - Concrete Walls:  Solidly fill space between frames and concrete with mineral-fiber insulation.

          - In-Place Concrete or Masonry Construction:  Secure frames in place with postinstalled expansion anchors.  Countersink anchors, and fill and make smooth, flush, and invisible on exposed faces.

          - Installation Tolerances:  Adjust hollow-metal door frames for squareness, alignment, twist, and plumb to the following tolerances:

            - Squareness:  Plus or minus 1/16 inch (1.6 mm), measured at door rabbet on a line 90 degrees from jamb perpendicular to frame head.

            - Alignment:  Plus or minus 1/16 inch (1.6 mm), measured at jambs on a horizontal line parallel to plane of wall.

            - Twist:  Plus or minus 1/16 inch (1.6 mm), measured at opposite face corners of jambs on parallel lines, and perpendicular to plane of wall.

            - Plumbness:  Plus or minus 1/16 inch (1.6 mm), measured at jambs at floor.

        - Glazing:  Comply with installation requirements in Section 088000 "Glazing" and with hollow-metal manufacturer's written instructions.

          - Secure stops with countersunk flat- or oval-head machine screws spaced uniformly not more than 9 inches (230 mm) o.c. and not more than 2 inches (51 mm) o.c. from each corner.

      - ADJUSTING AND CLEANING

        - Final Adjustments:  Remove and replace defective work, including hollow-metal work that is warped, bowed, or otherwise unacceptable.

        - Remove grout and other bonding material from hollow-metal work immediately after installation.

        - Prime-Coat Touchup:  Immediately after erection, sand smooth rusted or damaged areas of prime coat and apply touchup of compatible air-drying, rust-inhibitive primer.

END OF SECTION 08 12 13

FOR MDACC USE ONLY. DELETE THIS PAGE BEFORE ISSUING DOCUMENTS.

document revision history

| Issue | Date | Revision Description | Author |
| --- | --- | --- | --- |
|  | 20190301 | Original Issuance |  |
| Rev. 1 |  | . |  |
| Rev. 2 |  |  |  |
| Rev. 3 |  |  |  |
| Rev. 4 |  |  |  |
| Rev. 5 |  |  |  |