### TEMPLATE

### COMMISSIONING PLAN

### Construction Phase

(Insert Picture of Project Here)

Name of Project

Address of Project

City, State, Zip Code

Project Number

Prepared by:

Name of Company and preparer

Date

(Please note items in RED will need to be modified per each project)

Table of Contents

- Section	 Commissioning Plan	Page

- Overview	5

  - Purpose of the Commissioning Plan 	5

  - Related Commissioning  Specifications 	6

  - Abbreviations and Definitions	7

- Project Information	8

  - Project Information	8

- Commissioning Team	9

  - Organization Structure	9

  - Organizational Chart	9

  - Roles of Key Members	9

    - Owner Responsibilities 	9

    - Commissioning Authority (CxA)	9

    - Architect/Engineer’s Role and Responsibilities	9

    - Contractor	9

    - Test and Balance Firm	9

    - Commissioning Team	9

  - Commissioning Team Contact Information	10

    - MD Anderson	10

    - Architect/Engineer					10

    - Independent Contractors				10

    - Contractor 						10

    - Sub-Contractor 						10

- Commissioning Process	11

  - Commissioning Process Overview	11

  - Equipment To Be Commissioning	11

  - Commissioned Approach	13

  - Construction Phase	13

    - Coordination Kickoff Meeting				13

    - Cx Scheduling Meeting					13

    - Shop Drawing & Submittal Review			13

    - Cx Plan Submittal and Review				14

    - Finalize Test Procedures				14

    - Prefunctional  Review & Coordination		14

    - Prefunctional Reports	14

Table of Contents

- Section	 Commissioning Plan	 Page

    - Validation Test (14 Days) BAS Trend Log		15

    - Functional Test Scheduling Meeting			15

  - Testing and Training Phase	15

    - Functional Testing Performed				15

    - Test Results (Pass?)					15

    - Conduct Verification 					15

    - Integrated Systems Test					16

    - Operating and Maintenance Manuals			16

    - Training and System Orientation			16

    - Final Commissioning Report				16

  - Warranty Phase 	16

    - Conduct Deferred Verification 				16

    - Warranty Period						17

    - Amend Final Commissioning Report			17

- Prefunctional Check Test and Startup			17

  - Prefunctional Checklists  	17

  - Startup Checklist and Execution	19

  - Prefunctional Test Plan	19

- Functional Test and Verification Procedures	20

  - Testing Plan	20

  - Factory Tests

- 20

- Integrated Systems Test	20

  - Purpose of Integrated Systems Test Plan 	20

- Operating and Maintenance Manuals	21

- Owner Training and Orientation	22

  - Overview	22

  - Demonstration and Instructions	22

  - Training and Orientation	22

Table of Contents

- Section	 Commissioning Plan	 Page

- Reporting	24

  - Daily Reports	24

  - Commission Deficiency Log	24

- Warranties	24

  - Warranty Periods by Contractor/Vendor	24

  - Contractor/Vendor Data	25

- Schedule 	25

  - Project Schedule And Milestones	25

  - Sequential Priorities	25

  - Initial Schedule 	26

- Appendix									26

- 13.1     Organization Chart	27

  - Commissioning Log	28

  - Commissioning Flow Chart	31

  - Equipment Matrix (Obtain from Contractor)	33

  - Mechanical Flow Chart	35

  - Electrical System Test Flow Chart	36

  - Plumbing System Test Flow Chart	37

  - Life Safety Testing Flow Charts	38

  - Overall Staff Training and Orientation Plan	39

  - Training and Orientation Agenda Plan	43

  - Training and Orientation Record	45

  - Commissioning Deficiency Log	46

  - Commissioning Responsibility Flow Chart	47

  - Roles and Responsibility Matrix	48

Section 1.0 - Overview

1.1	Purpose of the Commissioning Plan

The purpose of the Commissioning (Cx) Plan-Construction Phase is to describe how systems will be operationally demonstrated and documented for complete working order.  During the construction phase, the Cx Plan provides the following:

- Direction for the commissioning tasks during construction

- Support to the specifications

- Templates for the application of the commissioning process

- Direction for the commissioning process during construction

- Resolution for design-related and construction issues

- Documentation of component and system check, test and start up

- Training of Owner’s operating staff on the systems

- Turnover of all Operating and Maintenance Manuals

The key to successful commissioning is the active pursuit of quality on this project throughout the duration of the contract.  Each member of the project team, not only those assigned to commissioning, are responsible for helping achieve this goal.

The Commissioning Plan provides guidelines for implementing MD Anderson's requirements  for the Project in accordance with the Contract Documents.  During commissioning, operational and functional performance testing of all systems will be verified for a period of 14 days without failure for compliance with the Contract Documents.  Equipment inspections and tests will be documented and operational and maintenance manuals, record documents, spare parts listings, special tools listings and other items will be verified.

The Commissioning Plan has been developed in accordance with the project specifications.

1.2	Related Commissioning Specifications

In accordance with the Project Specification 01 91 00 the following equipment and systems are to be commissioned.

Specification #		System Description

Division 01			General Requirements

01 77 00	Project Closeout Procedures

01 79 00	Demonstration and Training

01 91 00	General Commissioning Requirements

Divisions 02-43		(Add/Delete Sections per Project Requirements)

Division 20			Common Fire Suppression, Plumbing and HVAC Requirements

20 08 00			Fire Suppression, Plumbing and HVAC Systems Commissioning

20 08 13	Fire Suppression, Plumbing and HVAC Systems Pre-functional Checklist and Startups

20 08 16	Fire Suppression, Plumbing and HVAC System Functional Performance Testing

Division 23	Heating, Ventilating and Air Conditioning

23 05 93	System Testing, Adjusting, and Balancing For HVAC

Division 25	Integrated Automation

25 08 00	BAS Commissioning

Division 26	Electrical

26 08 00	Electrical Systems Commissioning

26 08 13	Electrical Systems Pre-functional Checklists and Startups

26 08 16	Electrical Systems Functional Performance Tests

Division 28	Electronic Safety and Security

28 00 00	Electronic Security

28 30 00	Fire Alarm and Smoke Detector Systems

1.3		Abbreviations and Definitions

The following are common abbreviations used in this document:

A/E		Architect/Engineer

AHJ		Authority Having Jurisdiction

BAS		Building Automation System

CDs		Construction Documents

CM		Construction Manager

Cx		Commissioning

CxA		Commissioning Authority

Cx Plan		Commissioning Plan

DID		Design Intent Document

EC		Electrical Contractor

ETA		Electrical Testing Agency

FAC		Fire Alarm Contractor

FPT		Functional Performance Test

FSC		Fire Suppression Contractor

IST		Integrated Systems Test

ISU		Issues Log

MC		Mechanical Contractor

MTA		Med / Lab Gas Testing Agency

NCR		Non Compliance Report Log

Owner		Owners Project Manager or Designated Representative

PFC		Pre-functional Checklist

Prefunctional		Check Testing & Startup

PWS		Project WorkSpace

RFI		Request for Information

SVC		Safety Verification Checklist

Sub		Subcontractor

TAB		Test, Adjust and Balance

Section 2.0 – Project Information

- The below information in this section is referenced from MD Anderson’s web page.

- 2.1	Project Information:

Insert a detailed description of the project and scope.

- GENERAL BUILDING INFORMATION:

- (Example)

- 12 story, 615,000 total building square feet

- 524,000 square feet of lab and office towers

- 218,298 gross square feet (labs, lab support, offices, conference/collaboration areas and building support services)

- 91,000 gross square feet two-story podium

- SPECIALTY AREAS:

- (Example)

- Animal housing / vivarium

- Cleanrooms

- Operating / patient treatment rooms

- Data centers

Section 3.0 – Commissioning Team

3.1	Organizational Structure

The successful implementation of the Commissioning Plan requires an organized commissioning team and an established working interface with MD Anderson Project Management representatives.  The commissioning team is made up of the Commissioning Authority – Name of Person and Company and the Quality Control Team, including the Quality Control Specialists working in conjunction with representatives from subcontractors, manufacturers, and suppliers to provide a quality project.  Commissioning Team members and their roles on this project are described in this section and shown on the Commissioning Team Organizational Chart.  If the Owner does not contract directly with a CxA, those responsibilities will be fulfilled by the Contractor.

  - Organizational Chart

We have included a copy of the project organization chart.  Please refer to Appendix 13.1 – Organization Chart. Please also refer to Appendix 13.13 for Commissioning responsibility flow chart, Appendix 13.14 for Roles and Responsibility Matrix

  - Roles of Key Members (Refer to Project Specification 01 91 00 for roles and responsibilities)

- Owner

- Commissioning Authority (CxA)

- Architect/Engineer’s Role and Responsibilities

- Contractor

- Test, Adjust, Balance Firm

- Commissioning Team

3.4 		Commissioning Team Contact Information

    - MD Anderson

| Name | Position/Organization | Phone # | Email Address |
| --- | --- | --- | --- |
| John Doe | Owner - Project Director | xxx-xxx-xxxx | Johndoe@1234.com |

    - Architect/Engineer

| John Doe | Principal – Project Director | xxx-xxx-xxxx | Johndoe@1234.com |
| --- | --- | --- | --- |

    - Independent Contractors

| John Doe | Independent – Project Director | xxx-xxx-xxxx | Johndoe@1234.com |
| --- | --- | --- | --- |

    - Contractor

| John Doe | CM | xxx-xxx-xxxx | Johndoe@1234.com |
| --- | --- | --- | --- |

    - Sub-Contractor

| John Doe | MC – My Company | xxx-xxx-xxxx | Johndoe@1234.com |
| --- | --- | --- | --- |

Section 4.0 – Commissioning Process

  - Commissioning Process Overview

Commissioning of each system will be performed by system.  Successful commissioning requires several steps.  These steps include:

- Equipment and material submittal and review

- Verification that equipment and materials meet the specified and approved submittal requirements

- Inspections and testing during installation to ensure quality installation and compliance in accordance to applicable building codes

- Prefunctional Checklist

- Turnover of operation and maintenance manuals

- Performance testing of system components singularly and systems as a whole

- Training

Refer to Project Specification 01 91 00 for requirements.

For some systems, the listed steps may not occur in the sequential order given.  Many times components of the commissioning process will take place concurrently.  In every case, the above requirements will be verified complete in order for final acceptance to be achieved. Not all steps are required for each system identified in specification 01 91 00.  Please refer to Apendix 13.2 Commissioning Log  that identifies the steps required for each specification section.

  - Equipment to be commissioned

The Equipment Matrix, prepared by the Contractor, will include all systems to be commissioned and will be used for process tracking throughout the construction phase of commissioning. The following general systems will be commissioned in this project. The following list has been copied from the equipment schedules shown in the Contract Drawings. All general references to equipment in this document refer only to equipment that is to be commissioned. Obtain a copy of the completed Equipment Matrix from the Contractor and include it within this document.

EXAMPLE:

HVAC Mechanical Systems (and all integral equipment controls)

 Administrative Area Air Handling Units

 Laboratory Air Handling Units and Energy Recovery Units

 Fan Coil Units and Computer Room AC Units

 Laboratory Exhaust Systems

 General Exhaust and Ventilation Fans

 Administrative Area Terminal Units

 Laboratory Tracking Venturi Systems

 Hydronic Pumps, Heat Exchangers and Accessories

 Heat Recovery Chiller

 Condensing Modular Boiler System

 Stairwell Pressurization Systems

 Building Automation System

Plumbing Systems

 Domestic water piping and fixtures

 Domestic Water Booster System

 Domestic Hot Water Heaters and Circulation Pumps

 Domestic Water Break Tank and controls

 Backflow Preventers and PRVs

 Water Softener System

 Lab/Hospital - Gas piping, valves, and monitoring components

 Lab/Hospital - Vacuum Compressor Skid

 Sanitary Waste / Vent piping

 Lab Waste / Vent Piping

 Storm water Piping

 Fuel Oil Piping and Delivery Systems

 Silver / Copper Ionization Systems

Electrical Systems

 Medium Voltage Switchgear and Substations

 Emergency Generator Systems

 Paralleling Switchgear and Generator Controls

 48 VDC Battery Systems

 Automatic and Manual Transfer Switches

 Uninterruptible Power Systems

 600 Volt Switchgear

 600 Volt Bus Distribution Systems

 Distribution Panels

 Panel boards

 Dry-type Transformers

 Lighting and Controls

 Branch Circuit Verification

 Starline Bus Systems

 Power Status and Monitoring System

 Grounding and Lightning Protection Systems

 Vertical Transportation Systems

 Radio Systems

Life Safety / Low Voltage Systems

 Fire Suppression Systems (wet, dry-type, pre-action)

 Fire Pump and Jockey Pump and associated controls

 Fire Alarm System

 Electronic Security and Access Control

 Security Surveillance

  - Commissioned Approach

The commissioning will be conducted with a three-phase approach.  The Cx plan has specific activities for each Cx phase.  The three-phases are as follows:

- Construction Phase

- Testing and Training Phase

- Warranty Phase

The Cx plan builds upon the activities of the previous phase.  As tests and the corresponding documentation is developed, it will be placed into the Cx Report.  When the three-phases are completed, the Cx Report will be submitted to the Owner labeled Final Commissioning Report.

The following is a brief description of the major activities listed in the Commissioning Plan Flow Chart.

On the following page is the project’s Appendix 13.3 – Commissioning Plan Flow Chart.

  - Construction Phase

    - Coordination Kickoff Meeting

The Construction Phase Commissioning Kickoff Meeting is intended to communicate to the Cx Team (which includes subcontractors) in the steps and intent of the commissioning process.  This meeting is held following the award of the contract and within the early stages of the project.  During the kickoff meeting, relationships of the individuals from each Cx Team member will be formulated.  The other primary purpose of the kickoff meeting is to communicate the complexity of the project and early on expected project milestones.

    - Cx Scheduling Meeting

Immediately following the Coordination Kickoff Meeting, develop a consensus of key commissioning project milestones.  These key milestones are integrated into the project’s master construction schedule.  The commissioning process is involved and complex.  The earlier the milestones are identified and integrated into the final phases of construction, the smoother the process will occur in the second half of the construction period

    - Shop Drawing & Submittal Review

The Contractor will submit the equipment and system shop drawing submittals to the Owner for review/comment/approval.  The review comments and approvals will be incorporated into the project.

Every piece of equipment and all associated materials are submitted to the Owner for review and approval.  All submittals are tracked via the Submittal Commissioning Log.  Please refer to Apendix 13.2 Commissioning Log for a sample copy.

A submittal is not considered closed until Approved, Approved as Noted designation is received.  Any submittal that does not receive one of the above action designations is revised in accordance with the review comments and resubmitted until the submittal can be deemed closed.  Factory testing and certifications of equipment to be commissioned are transmitted to the OR and tracked through the submittal process for record.

The submittal and request for information (RFI) processes record variances and clarifications to the Contract Documents.  The Owner will by issuance of requests for proposals (RFPs) and execution of contract Field Notice (FN) direct significant changes.  Contract drawings and specifications are continually updated as new information is received and copies are kept at the Contractors field office as well as on PWS. The current record drawings including posting of changes are maintained in the contractor’s field office these drawings are reviewed monthly with the Owner representatives.

As the submittal process for each item is completed, equipment is released for fabrication in compliance with the Contract Documents and submittal review comments.  When equipment and materials are received at the project site, they are checked against the approved submittal information and installed per the Contract Documents.   This verification is recorded on the pre-startup checklist developed for each piece of equipment.

During the installation of certain systems, inspections and testing will be ongoing to ensure quality of installation and compliance with applicable building codes.  Typically these test and inspection reports will be submitted as part of the PWS daily logs and observation reports.  Examples of these inspections and tests include the following:

- Site utility piping

- Flush testing sprinkler and plumbing for leakage testing

- Hydronic Pressure Tests

- Jurisdictional inspections for electrical, plumbing, sprinkler and elevator work

The records of these tests are maintained in Contractors Q.C office.

    - Cx Plan Submittal and Review

The Cx Plan will be submitted to the Owner for review/comment/approval.

    - Finalize Test Procedures

As procedures are submitted and approved, the procedures will become the control document to be used during the Testing and Training Phase.

    - Prefunctional Review & Coordination

In order to accomplish the required Prefuctional  and functional performance tests on an orderly basis, it will be important to preplan, review and coordinate the Prefuctional activities and schedule.  This coordination will take place during the weekly Cx meetings.

    - Prefunctional Reports

Prefunctional Reports are the documentation that the tests specified have been or would be conducted by the installing contractor.  These are the Prefunctional Checklist activities required prior to performing the functional tests.  For example the following are some examples of Prefunctional Checklists:

- Flush and clean water piping systems

- Hydrostatic pipe pressure tests

- Duct leakage tests

- Electrical point-to-point conductivity tests

- Power is wired and terminated to the electrical devices

These test reports will become part of the Cx Process.

    - Validation Test (14 Days) BAS Trend Log

As required in the specification and due to the accuracy of the systems, the contractor will operate the system for a period of 14 calendar days.  The computer based BAS system will be set up to perform a history trend log to record the key points of control for validation of the accuracy of the systems and their components prior to proceeding with Functional Testing.

    - Functional Test Scheduling Meeting

Having successfully completed the Prefunctional Checklist requirements, a schedule for the next phase, Testing and Training Phase, will be developed.  During the next phase, the systems will be tested.

  - Testing and Training Phase

4.5.1		Functional Testing Performed

At this point, the systems will be systemically functional performance tested.  The listed checklists in Section 14 -13 Commissioning Plans by Specification will be used as the basis of recording the tests performed.  It is recommended that the Owner’s O&M staff participate and observe this step of the process.  When the O&M staff participates in the observation process, they gain an understanding of the systems and the system’s locations prior to Training and Orientation.  It also gives the staff insight into the issues that were addressed during the Cx Phase.

    - Test Results (Pass?)

The recorded results will be compared to the expected results and the CxA will recommend to the Owner a pass or fail based on the results.  If the systems/component passes, then the checklist will be submitted as ready and will be included in the Final Cx Report.  If the system/component does not pass, then the Contractor will correct the deficiency, generate a deficiency log and re-perform the functional test.

    - Conduct Verification

The Contractor and the CxA will witness and document the verification test procedure for the major systems and for those that did not pass the first time as described above.  As the tests are witnessed, they will be filed in the daily report log.

If the system passes and is scheduled for the IST (Integrated Systems Test) then, the system will be readied for the Integrated Systems Test.  If the system fails, then an ISU (Issues Log) is generated, logged, corrected and retested.

It is again recommended that the Owner’s O&M staff participate and observe this step of the process for the same reasons listed in the above section.

    - Integrated Systems Test

The Integrated System Tests will be conducted to test that the systems will interact during two basic conditions.  Those conditions are as follows:

- From normal conditions to non-normal conditions

- From non-normal conditions to normal conditions

It is important to verify that the systems perform as designed.  Often the systems will operate correctly under normal to non-normal conditions.  However, sometimes systems will not return back to normal under the second condition.

Due to the importance of this step, please refer to Section 6 – Integrated Systems Testing Plan for a more detailed description of the plan.

    - Operating and Maintenance Manuals

The O&M manuals will be submitted for review and approval prior to Owner training per Specification 01 77 00.  The O&M manuals will be used as part of the training and system orientation program.

    - Training and System Orientation

Owner training and orientation on equipment and systems provided by the Contractor, is accomplished in three general steps:  They are as follows:

- Overall Plan

- Specific Training Agendas

- Training Record

Please refer to Section 9.0 – Training and Orientation of Owner’s Personnel for a more detail explanation of this section.

    - Final Commissioning Report

At the conclusion of the above listed steps, one digital copy of the tests reports and logs will be presented to the Owner/CxA for completion of the Commissioning Process.

  - Warranty Phase

    - Conduct Deferred Verification

There are frequently a small number of tests that could not be satisfactorily performed prior to turnover of the systems to the UTMDA.  This could be due to season weather conditions, i.e.: testing the heating system in the summer, cooling system in the winter, low process load or delay in user group fit out.

The deferred verification testing, corrective action documentation, tracking and retesting process is identical to the process listed in the Section 4.5Testing and Training Phase

    - Warranty Period

During the warranty period, any systems that need to serviced and repaired, as part of the warranty period will be handled by the installing contractor.  Telephone numbers and contact person will be listed in the warranty information that is submitted prior to the end of the project or as listed in Section 3.4 	Commissioning TeamContact Information.

    - Amend Final Commissioning Report

Any modifications made during the warranty period will be documented and forwarded to the Owner/CxA for amendment to the Final Commissioning Report.

Section 5.0 – Prefunctional Check, Test and Startup

  - Prefunctional Checklists

Prefunctional Checklists are important to ensure that the equipment and systems are hooked up, operational and that functional performance testing may progress without unnecessary delays.  Each piece of equipment receives full Prefunctional checkout by the Contractor.  No sampling strategies are used unless specifically listed by the Commissioning Plan or by Contract Documents.  In general, the Prefunctional Checklist for a given system must be successfully completed prior to formal functional performance testing of equipment or subsystems of the given system.

Prefunctional Checklists are primarily static inspections and procedures to prepare the equipment or systems for initial operation.  The following is a sample example:

- Oil levels OK

- Fan belt tension

- Labels affixed

- Gages in place

- Sensor calibration

However, some Prefunctional checklist items entail simple testing of the function of a component, piece of equipment or system.  The following is a sample example:

- Measure the voltage imbalance on a three phase device

- Point-to-point conductivity

- Hydro/gas pressure test piping systems

- Check electrical device rotation

The implication of Prefunctional Checklist refers to before functional testing.  Prefunctional Checklists augment and are combined with the manufacturer’s start-up checklists.  The installing contractors typically already perform some, if not many, of the Prefunctional Checklist items that would be recommended by the commissioning authority.

The primary value to the Prefunctional Checklist is in the form of putting the information down in writing.  Most contractors would not record their Prefunctional procedures.  The project requires that the Prefunctional procedures be documented in writing by the installing technician.  The CxA (Commissioning Authority) does not witness much of the Prefunctional Checklist Activities, except for testing of larger, more critical pieces of equipment. The General Contractor is required to witness and sign off checklist prior to requesting Functional testing from the CxA or the Owner.

A pre-start/startup checklist will be prepared by the Contractor and the subcontractors for every system and piece of equipment to be included on the project.  The checklists will be used to verify the status of the equipment and the readiness for system operations.  The checklist will also be a confirmation of the quality control checks and testing on the specific equipment and systems.

These quality control checks and testing includes the Submittal Review Checklists and Quality Field Inspection Checklists found in the Quality Control Plan.  These pre-start checklists must be completed prior to commissioning.  The checklists will be reviewed with each subcontractor and supplier to address specific project issues as the commissioning process proceeds

Prior to startup of each system, the following will be verified at a minimum:

- All utilities that are required to properly run the system are in place

- All components of the system needed to demonstrate performance are completed

- The system can be safely commissioned; this includes lockout/tag out and confined spaces procedures.

For an example, the utility requirements will include the electrical, mechanical and control systems that are to be present for the operation of the system.  For an air-handling unit (AHU), the heating hot water system may be required for complete operation; however the heat exchangers are NOT to be listed as a predecessor for startup of the AHU.  The heat exchangers are a predecessor of the heating hot water system.

The system completion requirements are as stated.  Example: for an air-handling unit (AHU), the ductwork system is required for complete operation.

Safety requirements for all startup and commissioning activities will be observed for each system.  These safety requirements include the following:

- The general requirements focusing on the physical building area in which the startup is to be performed.

- The specific requirements verifying the safety adequacy of the system and equipment being commissioned

Once the checklists have been completed and a review of the safety requirements has been performed, the contractor may then request in writing to the Owner permission to startup a system.

5.2	Startup Checklist and Execution

The parties responsibly for each part of startup and initial checkout are identified on the Commissioning Log.  Please refer to Appendix 13.2 – Commissioning Log for a list of responsible parties.

The following procedures will be used for this project:

- The listed Sub is responsible for performing the Cx procedure and checklist completion. The CxA reviews and formats the procedure.

- The Sub designated to develop the start-up plan obtains manufacture’s installation, start-up and checkout data, including actual field checkout sheets to be used by the field technicians.

- The Sub copies all pages with important instructional data and procedures from the star-up and checkout manuals and provided the documentation to the CxA, who then formats and adds a signature line in the column by each procedure or at the bottom of the form.

- The formatted pages along with the Prefunctional Checklists provided by the Subs will become the “Start-up and Checkout Plan”.

- For systems that may not have adequate manufacture’s start-up and checkout procedures, particularly for components being integrated with other systems/equipment, the Sub will provide the added necessary detail and documenting format for approval prior to execution.  Please refer to Section 6 – Integrated Systems Test.

To document the process of startup and checkout, the site technician performing the line item task initials and dates each paragraph of procedures and checks off items on the procedures as they are completed.  Only individuals having direct knowledge of a line item being completed shall check or initial the forms.

The Subs and vendors execute the checklist and test report and submit a signed copy of the completed startup and checklists to the Cx Authority (CxA).  The CxA will review checklists as necessary as the work progresses.

  - Prefunctional Test Plan

The following two flow charts were developed to assist the Cx Team in understanding the many functional steps required to complete the work.  Refer to Appendix 13.5Mechanical Systems Commissioning Plan Flow Chart , Appendix 13.6 – Electrical Systems Testing Flow Chart , Appendix 13.7 Plumbing Systems Testing Flow Chart and Appendix 13.8 Life Safety Testing Flow Chart respectively.

Section 6.0 – Functional Test and Verification Procedures

6.1                   Testing Plan

The Testing Plan and Log lists all tests and special inspections required by the contract, the responsible person or entity and the type and frequency of the test.  Test results are recorded on the test reports and furnished to the CxA representative.

Testing and inspections are performed to coincide with the approved Schedule and are coordinated by the Quality Control team to avoid any delays to the work.  The Testing Plan and Log and the Test Reports reference the appropriate activity number so that the tests can be scheduled properly to prevent the omission of a test and so that testing becomes a part of the "look ahead" process of Scheduling.

All tests and inspections shall include the following:

    - Project name and number.

    - Project location.

    - Product and specification section applicable.

    - Type of test/inspection.

    - Name of testing agency (if used).

    - Name of testing/inspecting personnel.

    - Date of test/inspection.

    - Observations regarding compliance.

    - Test method used.

    - Results of test.

    - Date of report.

    - Signature of testing/inspecting personnel.

6.2                    Factory Tests

Proper notification is given to the CxA representative for those items of equipment requiring factory tests per the technical specifications.  A list of all required factory tests is indicated in the submittal register.  Members of the Commissioning Team will witness factory tests where necessary. Completion of the required factory testing will be verified and documented in the pre-startup checklists.  Factory tests will be forwarded to the Owner as part of the submittal process.

Section 7.0 – Integrated Systems Test Plan

7.1	Purpose of Integrated Systems Test

The objective of the Integrated Systems Testing (IST) is to demonstrate that each system operates jointly and independently of other systems according to the contract documents. The Subs shall operate each system, jointly and independently of other systems through selected modes of operation including normal and emergency power modes and life safety interaction.

The TAB /CxA will develop the Integrated Systems Test in accordance with the specifications and submit to the CM/Contractor and Owner for review. The CM and Contractor will review the IST and submit to the Owner and A/E team for approval. Once approved, the test will be input into the Cx Plan and uploaded to PWS for use during the Cx process. The installing Subs should use the approved IST as a basis for any pre-testing that will occur prior to official Integrated Systems Testing.

The CxA schedules Integrated Systems Testing and coordinates all involved members of the Cx Team. The Owner will coordinate any necessary Owner personnel or facility impacts. For any given system, prior to performing an IST, the CxA waits until the Functional Performance Testing has been submitted with the necessary approvals, confirming that the system is complete or accepted by the Owner. The CxA and Contractor oversee the actual testing, which is usually performed by the installing Subs or vendor. The TAB/ CxA will facilitate and guide the test utilizing the approved IST.

The TAB/CxA documents the results of the test. Corrections of minor deficiencies identified are made during the tests at the discretion of the CxA and Contractor. Deficiencies or non-conformance issues are noted in the PWS issues log for tracking. If deficiencies cause the test to fail, the Subs shall correct deficiencies, notify the CxA and Contractor and update the PWS Issues Log certifying correction. The CxA and Contractor shall send an email update to the Cx Team and the Owner and coordinate scheduling of a re-test. Decisions regarding deficiencies and corrections are made at as low a level as possible, preferably between the CxA and Contractor and the Sub. For areas in dispute, final authority, besides the Owner, resides with the A/E. The TAB/CxA recommends acceptance of the completed test to the Owner and uploads the final documentation to PWS for record.

The Owner’s Operating and Maintenance (O&M) staff are encouraged to attend and participate in the testing process. The Contractor will notify the Owner, who will then notify the facility staff when the commissioning events will occur.

Section 8.0 – Operating and Maintenance Manuals

In accordance to Article 6 – 6.2.4 of the UGC – Requirements for Closeout Documents, and 01 77 00 Project Closeout Procedures - Provide two (2) bound copies and electronic copies of the Operating and Maintenance manuals to the Owner prior to performance testing and will become an important tool during the commissioning process.  The attached Commissioning Log in Appendix 13.2 identifies the Specification Sections requiring O&M manuals and Owner training.

Operating and Maintenance Manual documents must include, but are not limited to, approved submittals, manufacturer’s operating and maintenance instructions, brochures, shop drawings, performance curves and data sheets annotated to indicate equipment actually furnished (e.g. identifying impeller size, model, horsepower, etc),

Procedures, wiring and control diagrams, records of factory and field tests and device/controller settings and calibration, program lists or data compact discs, maintenance and warranty terms and contact information, spare parts listings, inspection procedures, emergency instructions, and other Operating and Maintenance documentation that may be useful to Owner.

Section 9.0 – Owner Training and Orientation

9.1		Overview

Training will be provided for all systems and equipment specified.  Schedules for training will be developed closer to the training dates.  The Owner will be given 10 Days’ notice of schedule. Each subcontractor in accordance with specification 01 79 00 will submit a detailed agenda of the training course. Training will begin after completion of the system performance testing and will be documented with the system demonstration and instruction report included in specification 01 79 00. Please refer to Appendix 13.2 Commissioning Log for identification of systems to receive training.

  - Demonstration and Instructions

A well-organized series of instruction and demonstration sessions is a central part of the commissioning process. The instructional portion of the commissioning will cover the following:

- Descriptions of each type of system including method of operation, capabilities and limitations

- Control systems.

- Inspection, service and maintenance requirements for each system.

- Operational monitoring and record keeping.

The demonstration portion of the commissioning will cover:

- Operation of each system, or a typical example when there are several similar ones in the building.

- Startup and shut down procedures, operation under all specified modes of control and sequence of operation and the correct procedures under an emergency (for example power failure) or abnormal conditions.

- Procedures necessary for effective operational monitoring.

9.3	Training and Orientation

Owner training and orientation on equipment and systems provided by the Contractor, is accomplished in three general steps:  They are as follows:

- Overall Plan

- Specific Training Agendas

- Training Record

Overall Plan:  After reviewing the specifications, the Owner and Cx Authority will fill out a table listing all the equipment that will have training and/or orientation.  Please refer to Appendix 13.9 – Overall Staff Training and Orientation Plan.  This form lists, among other things, the following:

- The trainee type and number

- Rigor of desired training by the Owner

- The primary responsible subcontractor

- The trainer’s company

- Columns for tracking training agendas.

Specific Training Agendas:  For each piece of equipment or system being trained, the Owner and the Cx Authority will fill out Section 1 of the Training and Orientation Agenda.  Please refer to Appendix 13.10 – Training and Orientation Agenda Plan.  This section includes some of the information from Appendix 13.9 regarding scope of training and the intended audience, for reference by the trainer in developing their agenda.  The Cx Authority develops a plan for including in the training session contractors/trainers from the different disciplines.  When appropriate, Section 2 of the form is filled out by listing the company names.  In particular, the controls contractor will provide brief training on controls, in the same session with the mechanical training for equipment controlled by the building automation system.

This form is then submitted to the Contractor who has their trainer fill out the rest of Section 2 & 3 of the form, Appendix 13.10 – Training and Orientation Agenda Plan.  This section describes the following:

- The subjects covered

- Duration of each subject

- The methods that will be used in the training

- Along with the names and qualifications of the trainer(s)

The trainer returns this form to the Contractor.  The Contractor, will submit it to the Owner.  The Owner will do the following:

- Make comments

- Approve subject to the comments

- Submit back to the Contractor

The Contractor provides the approved agenda to the trainer to use during the training.  The trainer provides a copy of the agenda to each trainee.

Training Record:  For each piece of equipment, prior to training, the Contractor will provide to their trainer(s) form Appendix 13.11 – Training Orientation Record.  On this form, the trainer documents each training session (duration and general subjects covered).  The trainer signs for the session and obtains the signature of each trainee.  The trainer also checks off subjects covered on the Agenda form.  Please refer to Appendix 13.11 – Training Orientation Record.  When training is complete, the Contractor provides a copy of Appendix 13.10 and 13.11 to the Owner for review and final approval by signature.  The Owner may witness any of the training sessions

Section 10.0 – Reporting

10.1		Daily Reports

Current and complete records of all on site and off site Quality Control activities and document flow are maintained as part of the Quality Control Plan.  This ensures that all project participants have current information. The commissioning activities will be documented and specifically identified in the quality control reports.

The Contractors Quality Control Team provides the following documentation to the Owner:

Testing Log

The Contractors Quality Control Team maintains a Testing Log. The Log will be all inclusive and leave areas in the spreadsheet to document the party responsible for performing the test, date test performed; date test results were forwarded to the Contracting Officer and the required frequency of the required tests. Subsequent submission will be attached to the last daily QAQC Report for each month.

Meeting Minutes

Weekly QC Meetings will be scheduled with all QC Specialists, Safety Manager, Project Superintendent, etc. to discuss at a minimum all items listed in Specification Section 01 45 00. As the commissioning process develops specific time will be set aside in the QC meeting to discuss and document commissioning activities and to update the team on scheduled pre-startup and startup inspections, functional performance testing and training.

10.2	Commissioning Deficiency Log

All work identified as non-conforming is documented and monitored in accordance with the procedure set forth below.

A non-conformance item is an in-progress procedure that defines materials or installation as unacceptable or out of compliance with the contract documents and the established level of quality.  All Contractor’s team members are responsible for reporting non-conformance that they observe to the Quality Control Manager or Specialists and the Project Superintendent.  The non-conformance items identified during the verification and performance testing will be specifically highlighted on the Commissioning Deficiency Log and addressed in the commissioning meetings. For larger projects, provide a separate Deficiency Log. A sample of the Commissioning Deficiency Log is included as Appendix 13.12.

Section 11.0 – Warranties

  - Warranty Periods by Contractor/Vendor

During the warranty period, seasonal testing and other deferred testing required will be completed according to the Specifications.  Tests will be executed and if any, deficiencies will be corrected by the appropriate Subs.  These tests will be witnessed the Cx Authority and Owner’s staff.  If required due to the tests, any final adjustments to the O&M manuals and record drawings will be made and coordinated by the Cx Authority.

At the end of the warranty period, at the 10-month point, the Cx Authority will meet with the Owner to review the current building operation and the condition of any outstanding issues related to the original and deferred commissioning plan.

11.2		Contractor/Vendor Data

For all listed warranties submitted at project closeout, the Contractor will include in the warranty manual the following information:

- Installing contractor’s name, address, telephone number(s)

- Vendor’s name, address, telephone number(s)

- Listed equipment

Section 12.0 – Schedule

12.1	Project Schedule AND MILESTONES

The work progress schedule calls for the project to be substantially complete by (Enter Date). It is not practical to construct and commission all building/systems/equipment at the same time.  Therefore, a progressive building schedule for pre and post Prefuctional and Functional checklists have been developed for the project.

The following milestone schedule communicates with all contractors and subcontractors a plan:

- Start-up Date: Date of initial equipment or device start-up by the Contractor

- Prefunctional Checklist completion date

- Functional Performance Test completion date

- Integrated Systems Test completion date

- Equipment Startups Begin –

- Substantial Completion date.

- Manufacturer’s warranties start date

- Warranty End Date: The date on which the asset warranty ends

  - Sequential Priorities

The general sequential priorities for commissioning systems are as follows:

- Equipment is not “temporarily” started for heating or cooling until pre-start checklist items and all manufacturers’ pre-start procedures are completed.

- No “temporary” equipment startups until the building moisture, dust and other environmental and facility integrity issues have been addressed.

- Functional testing is not begun until Prefunctional Checklists, startup and TAB are completed for a given system.  A phased testing approach is acceptable.

- The controls system and equipment it controls are not functionally tested until all points have been calibrated and Prefunctional Checklist/testing are completed.

- TAB is not performed until the controls system has been sufficiently functionally tested and approved by the Cx Authority and the controls contractor for TAB work.

- TAB is not performed until the envelope is completely enclosed and ceiling completed unless there is a ducted return system.

12.3	Initial Schedule

Task/Activity			Estimated Start		Estimated End

Date		Date

Initial scope meeting and final Cx Plan	(Insert Date)	(Insert Date)

Submittal obtained and reviewed	(Insert Date)	(Insert Date)

Begin construction site visits/inspections	(Insert Date)	(Insert Date)

Prefunctional Checklists developed and distributed	(Insert Date)	(Insert Date)

Startup and initial checkout plans	(Insert Date)	(Insert Date)

TAB – Water	(Insert Date)	(Insert Date)

TAB – Air	(Insert Date)              (Insert Date)

Functional Performance Tests developed and distributed	(Insert Date)	(Insert Date)

IST	(Insert Date)	(Insert Date)

O&M documentation review and verification	(Insert Date)	(Insert Date)

Training and training verification	(Insert Date)	(Insert Date)

Final commissioning report and acceptance per 01 91 00 	(Insert Date)	(Insert Date)

Seasonal testing	(Insert Date)	(Insert Date)

Amended Cx Report	(Insert Date)	(Insert Date)

Section 13.0 – Appendix

  - Organization Chart

  - Commissioning Log

  - Commissioning  Plan Flow Chart

  - Equipment Matrix (Obtain from Contractor)

  - Mechanical Flow Chart

  - Electrical Flow Chart

  - Plumbing Flow Chart

  - Life Safety Flow Chart

  - OVERALL STAFF TRAINING AND ORIENTATION PLAN

  - Training and Orientation Agenda Plan

  - Training and Orientation Record

  - COMMISSIONING  DEFICIENCIY LOG

  - Commissioning Responsibility Flow Chart

  - ROLES AND RESPONSIBILITY MATRIX