## Sheet1
SERVICE | VALVE TYPE | ON PLAN DRAWING - TAG WITH ASSET NUMBER | ON O&M RISER DIAGRAM | In Model | On Asset (TAG) Matrix & Maximo | Comments | Published Date: February 4, 2025
[7 empty] | LEGEND: | "X" = Yes
PLUMBING | [7 empty] | Greyed Out = No
DHW
| ISOLATION VALVES FOR WATER HEATERS | X | X | X | WITHIN 3', "NO"
| ISOLATION VALVES ON RISER BRANCH SUPPLY AND RETURN | X | X | X | X
DCW
| MAIN SHUTOFF IN LEVEL 1 PUMP ROOM | X | X | X | X
| TANK FILL VALVE IN LEVEL 1 PUMP ROOM | X | X | X | X
| ALL RISER ISOLATION VALVES AT RISER BASES | X | X | X | X
| ISOLATION VALVES ON RISER BRANCH SUPPLY | X | X | X | X
RO WATER (TREAT DI SAME AS RO)
| ISOLATION VALVES ON PRODUCTION EQUIPMENT LEVEL 8- SUPPLY AND RETURN | X | X | X
| ISOLATION VALVES ON RISER BRANCH SUPPLY AND RETURN (ROS AND ROR) | X | X | X | X
BULK GASES (MGTF)
| ISOLATION VALVES AT EACH BULK TANK OR CYLINDER MANIFOLD | X | X | X | X
| ISOLATION VALVES ON EACH PIPE ENTERING THE BUILDING | X | X | X | X
| SHUTOFF AT BASE OF EACH RISER | X | X | X | X
| SHUTOFF VALVE FOR BRANCHES FROM RISER AT EACH LEVEL | X | X | X | X
| SHUTOFF VALVES FOR EACH GAS AT LEVELS | X | X | X | X
LIQUID NITROGEN
| SHUTOFF VALVE AT BULK TANK | X | X | X | "YES", INCLUDING LOCATIONS INSIDE BUILING WHERE IT IS DISPENSED, AND ANY EMERGENCY SHUT OFF VALVES
VACUUM (MEDICAL AIR, WASTE ANESTHETIC GASES *WAGS* TREAT SAME AS VACCUM) |  |  |  |  | X
| MAIN VALVE AT VACUUM PUMP | X | X | X | X
| ISOLATION VALVE FROM RISER AT EACH LEVEL | X | X | X | X
CHW
| MAINS WHERE TECO ENTERS BUILDING SUPPLY AND RETURN | X | X | X | X
| ISOLATION VALVES FROM RISER BRANCHES AT EACH FLOOR SUPPLY AND RETURN | X | X | X | X
| ISOLATION VALVES AT FLOW METERS | X | X | X | X
| ISOLATION VALVES AT EACH HRC | X | X | X | X
| ISOLATION VALVES AT EACH HEX | X | X | X | X
| ISOLATION VALVES AT EACH PUMP | X | X | X | X
| VALVES WHERE MAIN CHW HEADERS MEET IN PENTHOUSE | X | X | X | X
| MAIN SHUTOFF AT EACH AIR HANDLING UNIT | X | X | X | X
| TECO VALVES | X | X | X | X
HHW
| ISOLATION VALVES AT EACH BOILER | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| ISOLATION VALVES FROM RISER BRANCHES AT EACH FLOOR SUPPLY AND RETURN | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| ISOLATION VALVES AT FLOW METERS | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| ISOLATION VALVES AT EACH HRC | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| ISOLATION VALVE AT EACH PUMP | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| BYPASS VALVE IN PENTHOUSE | X | X | X | ARE THESE AUTOMATED OR MODULATED IN ANY WAY? THEN "YES" BUT IF PURE ISOLATION VALVES, THEN "NO"
| MAIN SHUTOFF AT EACH AIR HANDLING UNIT | X | X | X
PCHW
| ISO VALVES FROM RISER BRANCHES AT EACH FLOOR SUPPLY AND RETURN | X | X | X | X
| ISO VALVES AT FLOW METERS | X | X | X | X
| ISO VALVES AT EACH HRC | X | X | X | X
| ISO VALVES AT EACH HEX | X | X | X | X
CHECK VALVES/ VALVES IN MAN. EQUIPM/ FAUCETS/ HOSE BIBS/ NEEDLE VALVES/ GUAGE COCKS/ HVAC TERMINAL DEVICES/ SIMILAR CONNECTIONS OF END-USE FIXTURES AND UNITS |  | IF ATTACHED TO UNIT THEN "NO". IF LOCATED IN CEILING, OR SEPARATE FROM UNIT, THEN "YES". | X | X | IF ATTACHED TO UNIT THEN "NO". IF LOCATED IN CEILING, OR SEPARATE FROM UNIT, THEN "YES".
MANUAL VENT AND DRAIN VALVES |  | X | X | X | X
NATURAL GAS | CRITICAL ISO VALVES | X | X | X | X
DW BFP |  | X | X | X | X
RELIEF VALVES |  | X | X |  | X
BALANCING VALVES |  | X | X |  | X
FIRE PROTECTION | Life Safety Valves | X | X | X |  | STILL INCLUDE IN EQUIPMENT MATRIX; DOES NOT GO INTO MAXIMO; Naming convention is: Building Acronym Floor Location (Room number in) (Room number by if corridor) (Stairwell) Size of Valve (*NOTE: This is different than how the fire alarm should be formatted for valve tamper switches that is in our fire alarm specification.)
FIRE PROTECTION | BFP | X | X | X | X
FUEL OIL | CRITICAL ISO VALVES | X | X | X | X
CONTROL VALVES |  | X | X | X | X
INTEGRAL TO SKID EQUIPMENT VALVES
MDA NOTES:
FLUSH VALVES, VALVES UNDER SINKS NOT NEEDED
DI & RO TREAT SAME
SANITARY VALVES - VALVES THAT CUT OFF GRAVITY FEED THAT DIVERT TO EJECTOR PUMP YES INCLUDE THESE IN MODEL & MAXIMO
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "ON SUB MATRIX AND PLAN DRAWING-TAG WITH ASSET NUMBER"
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed "critical vlv spec"
Note on B5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expanded "ISOS" to Isolation Valves (TYP)
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sticking with "X" convention for "Yes", unless the cell contains additional details (TYP)
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sticking with "<blank cell>" convention for "No", unless the cell contains additional details (TYP)
Note on F22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated from "YES & WHERE DISPENSED INSIDE BLDG & ANY EMERG SHUT OFF VALVES"
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Modified from "VACUUM (MEDICAL AIR, WASTE ANEST GAS *WAGS* TREAT SAME AS VACCUM)"